## BOP-PLC-CP
EQUIPMENT |  |  |  | TAGS |  |  |  | I/O MODULES
EQUIPMENT ID | EQUIPMENT TYPE | EQUIPMENT DESCRIPTION | CLASSIFIED ENVIRONMENT | TAG NAME | TAG DESCRIPTION | SIGNAL TYPE | ALARMS | MODULE SLOT # | CHANNEL | DETAILS (to be deleted)
BL-1 | BLOWER | DIG BLWR | NO | BL_1.RUN_CMD | DIG BLWR RUN COMMAND | DO | NO | 10 | 4 | ON LINE BETWEEN DMT ZONE AND FLARE
BL-1 | BLOWER | DIG BLWR | NO | BL_1.SPD_CMD | DIG BLWR SPEED RAW COMMAND | AO | NO | 5 | 0 | ON LINE BETWEEN DMT ZONE AND FLARE
BL-1 | BLOWER | DIG BLWR | NO | BL_1.RUN_ST | DIG BLWR RUNNING STATUS | DI | FTS | 8 | 2 | ON LINE BETWEEN DMT ZONE AND FLARE
BL-1 | BLOWER | DIG BLWR | NO | BL_1.FLT_ST | DIG BLWR FAULT STATUS | DI | FLT | 8 | 3 | ON LINE BETWEEN DMT ZONE AND FLARE
BL-1 | BLOWER | DIG BLWR | NO | BL_1.MAN_ST | DIG BLWR AUTO/MANUAL STATUS | DI | NO | 9 | 0 | CHANGE FROM TO CLEAR FAULT COMMAND? OR REMOVE ? OPERATION STATUS, FALSE = MANUAL, TRUE = AUTO
BL-1 | BLOWER | DIG BLWR | NO | BL_1.SPD_FBK | DIG BLWR SPEED FEEDBACK | HART - P | SPD-MIS | 4 | 2 | 4 WIRE SELF POWERED XMTR? NEED TO CONFIRM OUTPUT TYPE
CV1001 | CONTROL VALVE (FV) | FLARE CONTROL VALVE | YES | CV_1001.POS_CMD | FLARE CONTROL VALVE POSITION RAW COMMAND | AO | NO | 5 | 1 | ON LINE FROM DMT ZONE (H2S MEDIA) TO FLARE
CV1001 | CONTROL VALVE (FV) | FLARE CONTROL VALVE | YES | CV_1001.POS_OP | FLARE CONTROL VALVE IN OPEN POSITION | DI | FTO | 8 | 6 | ON LINE FROM DMT ZONE (H2S MEDIA) TO FLARE
CV1001 | CONTROL VALVE (FV) | FLARE CONTROL VALVE | YES | CV_1001.POS_CL | FLARE CONTROL VALVE IN CLOSED POSITION | DI | FTC | 8 | 7 | ON LINE FROM DMT ZONE (H2S MEDIA) TO FLARE
CV3001 | CONTROL VALVE (FV) | DIG BLWR CONTROL VALVE | YES | CV_3001.POS_CMD | CONTROL VALVE POSITION RAW COMMAND | AO | NO | 5 | 2 | update description
CV3001 | CONTROL VALVE (FV) | DIG BLWR CONTROL VALVE | YES | CV_3001.POS_OP | DIG BLWR CONTROL VALVE IS IN OPEN POSITION | DI | FTO | 8 | 8 | update description
CV3001 | CONTROL VALVE (FV) | DIG BLWR CONTROL VALVE | YES | CV_3001.POS_CL | DIG BLWR CONTROL VALVE IS IN CLOSED POSITION | DI | FTC | 8 | 9 | update description
CV3002 | CONTROL VALVE (FV) | PROCESS FEED CONTROL VALVE | YES | CV_3002.POS_CMD | PROCESS FEED CONTROL VALVE POSITION RAW COMMAND | AO | NO | 6 | 0 | ON LINE FROM DVO TO DMT BLOWER
CV3002 | CONTROL VALVE (FV) | PROCESS FEED CONTROL VALVE | YES | CV_3002.POS_OP | PROCESS FEED CONTROL VALVE IS IN OPEN POSITION | DI | FTO | 8 | 10 | ON LINE FROM DVO TO DMT BLOWER
CV3002 | CONTROL VALVE (FV) | PROCESS FEED CONTROL VALVE | YES | CV_3002.POS_CL | PROCESS FEED CONTROL VALVE IS IN CLOSED POSITION | DI | FTC | 8 | 11 | ON LINE FROM DVO TO DMT BLOWER
CV3003 | CONTROL VALVE (FV) | PROCESS BIO FLARE CONTROL VALVE | YES | CV_3003.POS_CMD | PROCESS BIO FLARE CONTROL VALVE POSITION RAW COMMAND | AO | NO | 6 | 1 | ON LINE FROM DMT ZONE (H2S MEDIA) TO FLARE
CV3003 | CONTROL VALVE (FV) | PROCESS BIO FLARE CONTROL VALVE | YES | CV_3003.POS_OP | PROCESS BIO FLARE CONTROL VALVE IN OPEN POSITION | DI | FTO | 8 | 12 | ON LINE FROM DMT ZONE (H2S MEDIA) TO FLARE
CV3003 | CONTROL VALVE (FV) | PROCESS BIO FLARE CONTROL VALVE | YES | CV_3003.POS_CL | PROCESS BIO FLARE CONTROL VALVE IN CLOSED POSITION | DI | FTC | 8 | 13 | ON LINE FROM DMT ZONE (H2S MEDIA) TO FLARE
CV3005 | CONTROL VALVE (FV) | LAG RNG/BIO CONTROL VALVE | YES | CV_3005.POS_CMD | LAG RNG/BIO CONTROL VALVE POSITION RAW COMMAND | AO | NO | 6 | 2 | ON LINE FROM DMT ZONE (REJECT GAS) TO LAGOON WSP3
CV3005 | CONTROL VALVE (FV) | LAG RNG/BIO CONTROL VALVE | YES | CV_3005.POS_OP | LAG RNG/BIO CONTROL VALVE IN OPEN POSITION | DI | FTO | 8 | 14 | ON LINE FROM DMT ZONE (REJECT GAS) TO LAGOON WSP3
CV3005 | CONTROL VALVE (FV) | LAG RNG/BIO CONTROL VALVE | YES | CV_3005.POS_CL | LAG RNG/BIO CONTROL VALVE IN CLOSED POSITION | DI | FTC | 8 | 15 | ON LINE FROM DMT ZONE (REJECT GAS) TO LAGOON WSP3
CV3007 | CONTROL VALVE (FV) | LAG TO H2S MEDIA CONTROL VALVE | YES | CV_3007.POS_CMD | POSITION RAW COMMAND | AO | NO | 7 | 0 | UPDATE DESCRIPTION
CV3007 | CONTROL VALVE (FV) | LAG TO H2S MEDIA CONTROL VALVE | YES | CV_3007.POS_OP | CONTROL VALVE IN OPEN POSITION | DI | FTO | 9 | 1 | UPDATE DESCRIPTION
CV3007 | CONTROL VALVE (FV) | LAG TO H2S MEDIA CONTROL VALVE | YES | CV_3007.POS_CL | CONTROL VALVE IN CLOSED POSITION | DI | FTC | 9 | 2 | UPDATE DESCRIPTION
CV3008 | CONTROL VALVE (FV) | DIG TO H2S MEDIA CONTROL VALVE | YES | CV_3008.POS_CMD | POSITION RAW COMMAND | AO | NO | 7 | 1 | UPDATE DESCRIPTION
CV3008 | CONTROL VALVE (FV) | DIG TO H2S MEDIA CONTROL VALVE | YES | CV_3008.POS_OP | CONTROL VALVE IN OPEN POSITION | DI | FTO | 9 | 3 | UPDATE DESCRIPTION
CV3008 | CONTROL VALVE (FV) | DIG TO H2S MEDIA CONTROL VALVE | YES | CV_3008.POS_CL | CONTROL VALVE IN CLOSED POSITION | DI | FTC | 9 | 4 | UPDATE DESCRIPTION
CV3009 | CONTROL VALVE (FV) | DIG TO LAG CONTROL VALVE | YES | CV_3009.POS_CMD | POSITION RAW COMMAND | AO | NO | 7 | 2 | UPDATE DESCRIPTION
CV3009 | CONTROL VALVE (FV) | DIG TO LAG CONTROL VALVE | YES | CV_3009.POS_OP | CONTROL VALVE IN OPEN POSITION | DI | FTO | 9 | 5 | UPDATE DESCRIPTION
CV3009 | CONTROL VALVE (FV) | DIG TO LAG CONTROL VALVE | YES | CV_3009.POS_CL | CONTROL VALVE IN CLOSED POSITION | DI | FTC | 9 | 6 | UPDATE DESCRIPTION
FIT3001 | FLOW TRANSMITTER | O2 RCVR TANK FLOW | NO | FIT_3001.F_RS | O2 RCVR TANK FLOW RATE RAW | AI | LL = X L = X H = X HH = X | 1 | 0 | E&H Prosonic G500 PASSIVE OUTPUT, 2 WIRE LOOP POWERED XMTR
FIT3002 | FLOW TRANSMITTER | LAG BIO FLOW | NO | FIT_3002.F_RS | LAG BIO FLOW RATE RAW | AI | LL = X L = X H = X HH = X | 1 | 1 | E&H Prosonic G500 PASSIVE OUTPUT, 2 WIRE LOOP POWERED XMTR
FIT3003 | FLOW TRANSMITTER | PROCESS BIO FLOW | NO | FIT_3003.F_RS | PROCESS BIO FLOW RATE RAW | AI | LL = X L = X H = X HH = X | 1 | 2 | E&H Prosonic G500 PASSIVE OUTPUT, 2 WIRE LOOP POWERED XMTR
FIT3004 | FLOW TRANSMITTER | RNG REJECT FLOW | NO | FIT_3004.F_RS | RNG REJECT FLOW RATE RAW | AI | LL = X L = X H = X HH = X | 1 | 3 | E&H Prosonic B200 PASSIVE OUTPUT, 2 WIRE LOOP POWERED XMTR
FIT3005 | FLOW TRANSMITTER | LAG RNG/BIO FLOW | NO | FIT_3005.F_RS | LAG RNG/BIO FLOW RATE RAW | AI | LL = X L = X H = X HH = X | 1 | 4 | E&H Prosonic G500 OR B200 PASSIVE OUTPUT, 2 WIRE LOOP POWERED XMTR
FIT3008 | FLOW TRANSMITTER | DMT VENT TO ATMOSPHERE FLOW | NO | FIT_3008.F_RS | DMT VENT TO ATMOSPHERE FLOW RATE RAW | AI | LL = X L = X H = X HH = X | 1 | 5 | E&H Prosonic G500 OR B200 PASSIVE OUTPUT, 2 WIRE LOOP POWERED XMTR
FLARECP | FLARE CONTROL PANEL | FULLY ENCLOSED BIOGAS FLARE (FEF) CONTROL SYSTEM | NO | FLR_CP.SYS_ALM | FLARE CONTROL SYSTEM ALARM | DI | FLT | 8 | 4 | ADDED FROM FEF CONTROL SYSTEM DWGs
FLARECP | FLARE CONTROL PANEL | FULLY ENCLOSED BIOGAS FLARE (FEF) CONTROL SYSTEM | NO | FLR_CP.RUN_ST | FLARE CONTROL SYSTEM RUNNING STATUS | DI | FTS | 8 | 5 | ADDED FROM FEF CONTROL SYSTEM DWGs
FLARECP | FLARE CONTROL PANEL | FULLY ENCLOSED BIOGAS FLARE (FEF) CONTROL SYSTEM | NO | FLR_CP.STRT_CMD | FLARE CONTROL SYSTEM START SIGNAL | DO | NO | 10 | 5 | ADDED FROM FEF CONTROL SYSTEM DWGs
FLARECP | FLARE CONTROL PANEL | FULLY ENCLOSED BIOGAS FLARE (FEF) CONTROL SYSTEM | NO | FLR_CP.INT_STP | FLARE CONTROL SYSTEM INTERLOCK STOP SIGNAL | DO | NO | 10 | 6 | ADDED FROM FEF CONTROL SYSTEM DWGs
GC3001 | GAS CHROMATOGRAPH E&H Prosonic G500 | O2 RCVR TANK GAS | NO | GC_3001.CH4_RS | O2 RCVR TANK GAS CH4 RAW | HART - P | LL = X L = X H = X HH = X | 3 | 0 | DVOBIO GC (CH4, CO2) DVO DIGESTER OUTLET PASSIVE OUTPUT, 2 WIRE LOOP POWERED XMTR
GC3001 | GAS CHROMATOGRAPH E&H Prosonic G500 | O2 RCVR TANK GAS | NO | GC_3001.CO2_RS | O2 RCVR TANK GAS CO2 RAW | HART - S | LL = X L = X H = X HH = X | 3 | 0 | DVOBIO GC (CH4, CO2) DVO DIGESTER OUTLET
GC3002 | GAS CHROMATOGRAPH | LAG BIO GAS | NO | GC_3002.CH4_RS | LAG BIO GAS CH4 RAW | HART - P | LL = X L = X H = X HH = X | 3 | 1 | LBIO GC (CH4, CO2, O2, N2) LAGOON OUTLET PASSIVE OUTPUT, 2 WIRE LOOP POWERED XMTR
GC3002 | GAS CHROMATOGRAPH | LAG BIO GAS | NO | GC_3002.CO2_RS | LAG BIO GAS CO2 RAW | HART - S | LL = X L = X H = X HH = X | 3 | 1 | LBIO GC (CH4, CO2, O2, N2) LAGOON OUTLET
GC3002 | GAS CHROMATOGRAPH | LAG BIO GAS | NO | GC_3002.N2_RS | LAG BIO GAS N2 RAW | HART - S | LL = X L = X H = X HH = X | 3 | 1 | LBIO GC (CH4, CO2, O2, N2) LAGOON OUTLET
GC3002 | GAS CHROMATOGRAPH | LAG BIO GAS | NO | GC_3002.O2_RS | LAG BIO GAS O2 RAW | HART - S | LL = X L = X H = X HH = X | 3 | 1 | LBIO GC (CH4, CO2, O2, N2) LAGOON OUTLET
GC3003 | GAS CHROMATOGRAPH E&H Prosonic G500 | PROCESS BIO GAS | NO | GC_3003.CH4_RS | PROCESS BIO GAS CH4 RAW | HART - P | LL = X L = X H = X HH = X | 3 | 2 | FLAREBIO FIT FLARE - BIOGAS PASSIVE OUTPUT, 2 WIRE LOOP POWERED XMTR
GC3003 | GAS CHROMATOGRAPH E&H Prosonic G500 | PROCESS BIO GAS | NO | GC_3003.CO2_RS | PROCESS BIO GAS CO2 RAW | HART - S | LL = X L = X H = X HH = X | 3 | 2 | FLAREBIO FIT FLARE - BIOGAS
GC3004 | GAS CHROMATOGRAPH E&H Prosonic B200 | RNG FLARE GAS | NO | GC_3004.CH4_RS | RNG FLARE GAS CH4 RAW | HART - P | LL = X L = X H = X HH = X | 3 | 3 | RNG.FLARE GC (CH4, CO2) FLARE - PRODUCT GAS PASSIVE OUTPUT, 2 WIRE LOOP POWERED XMTR
GC3004 | GAS CHROMATOGRAPH E&H Prosonic B200 | RNG FLARE GAS | NO | GC_3004.CO2_RS | RNG FLARE GAS CO2 RAW | HART - S | LL = X L = X H = X HH = X | 3 | 3 | RNG.FLARE GC (CH4, CO2) FLARE - PRODUCT GAS
GC3005 | GAS CHROMATOGRAPH E&H Prosonic G500 OR B200 | LAG RNG/BIO GAS | NO | GC_3005.CO2_RS | LAG RNG/BIO GAS CO2 RAW | HART - S | LL = X L = X H = X HH = X | 4 | 0 | RECIRC GC (CH4, CO2) RECIRCULATED GAS FROM DVO AND PRODUCT GAS TO LAGOON
GC3005 | GAS CHROMATOGRAPH E&H Prosonic G500 OR B200 | LAG RNG/BIO GAS | NO | GC_3005.CH4_RS | LAG RNG/BIO GAS CH4 RAW | HART - P | LL = X L = X H = X HH = X | 4 | 0 | RECIRC GC (CH4, CO2) RECIRCULATED GAS FROM DVO AND PRODUCT GAS TO LAGOON PASSIVE OUTPUT, 2 WIRE LOOP POWERED XMTR
GC3008 | GAS CHROMATOGRAPH | DMT VENT TO ATMOSPHERE GAS | NO | GC_3008.CO2_RS | DMT VENT TO ATMOSPHERE GAS CO2 RAW | HART - S | LL = X L = X H = X HH = X | 4 | 1 | NOT SHOWN ON P&ID
GC3008 | GAS CHROMATOGRAPH | DMT VENT TO ATMOSPHERE GAS | NO | GC_3008.CH4_RS | DMT VENT TO ATMOSPHERE GAS CH4 RAW | HART - P | LL = X L = X H = X HH = X | 4 | 1 | NOT SHOWN ON P&ID PASSIVE OUTPUT, 2 WIRE LOOP POWERED XMTR
PIT3001 | PRESSURE TRANSMITTER | O2 RCVR TANK PRESSURE - DVO TO BLOWER 1 | NO | PIT_3001.P_RS | RNG PRESSURE RAW | AI | L = X H = X | 1 | 6 | Rosemount 3051TG PASSIVE OUTPUT, 2 WIRE LOOP POWERED XMTR NEW ADDITION PER EMAIL UPDATE
PWR-MAIN | MAIN CP PWR - INPUT RELAY | AC FAULT ALARM RELAY | NO | CR_01.ACFLT | AC FAULT ALARM RELAY SIGNAL | DI | FLT | 8 | 0 | NOT SURE IF WE WANT TO KEEP IT ON THIS LIST
PWR-UPS | UPS PWR - INPUT RELAY | UPS FAULT ALARM RELAY | NO | CR_02.UPS | UPS FAULT ALARM RELAY SIGNAL | DI | FLT | 8 | 1 | NOT SURE IF WE WANT TO KEEP IT ON THIS LIST
Note on G11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Typically an open/close valve isnt going to have analog position feedback… it is available but usually its just ZSO/ZSC
Note on G17: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Typically an open/close valve isnt going to have analog position feedback… it is available but usually its just ZSO/ZSC
Note on G20: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Typically an open/close valve isnt going to have analog position feedback… it is available but usually its just ZSO/ZSC
Note on G23: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Typically an open/close valve isnt going to have analog position feedback… it is available but usually its just ZSO/ZSC

## LGN-PLC-CP
EQUIPMENT |  |  |  | TAGS |  |  |  | I/O MODULES |  |  | ACTION REQUIRED: REVIEW OR RESPONSE NEEDED.
EQUIPMENT ID | EQUIPMENT TYPE | EQUIPMENT DESCRIPTION | CLASSIFIED ENVIRONMENT | TAG NAME | TAG DESCRIPTION | SIGNAL TYPE | ALARMS | MODULE SLOT # | CHANNEL | DETAILS (to be deleted) | TAG UPDATED SINCE LAST REVIEW.
AC_001 | AIR COMPRESSOR | AIR COMPRESSOR FEEDER | NO | AC_001.RUN_ST | AIR COMPRESSOR RUN STATUS | DI | FTS | 6 | 3 | NEED TO CONFIRM WIRING
AC_001 | AIR COMPRESSOR | AIR COMPRESSOR FEEDER | NO | AC_001.UF001 | AIR COMPRESSOR FAILURE SIGNAL | DI | FLT | 6 | 4 | NEED TO CONFIRM WIRING
AC_001 | AIR COMPRESSOR | AIR COMPRESSOR FEEDER | NO | AC_001.RUN_CMD | AIR COMPRESSOR RUN COMMAND | DO | NO | 8 | 0 | Provided documentation references both the MAM-6090 and MAM-200 controllers. MAM-6090 control has been assumed for design purposes, requiring one dry contact for Run/Stop control. If the package utilizes a MAM-200 controller, additional outputs will be required, as separate Start and Stop command inputs are provided. MAM-6090: APPLY SIGNAL FOR 5 SECONDS TO START. REMOVE AND REAPPLY SIGNAL FOR 5 SECONDS TO STOP.
AC_001 | AIR COMPRESSOR | AIR COMPRESSOR FEEDER | NO | AC_001.STP_CMD | AIR COMPRESSOR STOP COMMAND | DO | NO | 8 | 1 | Provided documentation references both the MAM-6090 and MAM-200 controllers. MAM-6090 control has been assumed for design purposes, requiring one dry contact for Run/Stop control. If the package utilizes a MAM-200 controller, additional outputs will be required, as separate Start and Stop command inputs are provided. MAM-6090: APPLY SIGNAL FOR 5 SECONDS TO START. REMOVE AND REAPPLY SIGNAL FOR 5 SECONDS TO STOP.
AC_010A | AFTER COOLER | BLWR-A DISCHARGE AFTER COOLER | NO | AC_010A.SPD_FBK | BLWR-A DISCHARGE AFTER COOLER SPEED FEEDBACK | AI | LL = X L = X H = X HH = X | 1 | 3 | ASSUME SINGLE-ENDED (LOOP-POWERED) SIGNAL NEED TO UPDATE ALARM LIMITS
AC_010A | AFTER COOLER | BLWR-A DISCHARGE AFTER COOLER | NO | AC_010A.SPD_CMD | BLWR-A DISCHARGE AFTER COOLER SPEED COMMAND | AO | NO | 5 | 4 | CONFIRM WIRING
AC_010A | AFTER COOLER | BLWR-A DISCHARGE AFTER COOLER | NO | AC_010A.RUN_ST | BLWR-A DISCHARGE AFTER COOLER RUN STATUS | DI | FTS | 7 | 6 | 0 = STOPPED, 1 = RUNNING
AC_010A | AFTER COOLER | BLWR-A DISCHARGE AFTER COOLER | NO | AC_010A.FLT_ST | BLWR-A DISCHARGE AFTER COOLER FAULT STATUS | DI | FLT | 7 | 7 | 0 = NORMAL, 1 = FAULT
AC_010A | AFTER COOLER | BLWR-B DISCHARGE AFTER COOLER | NO | AC_010A.RUN_CMD | BLWR-A DISCHARGE AFTER COOLER RUN COMMAND | DO | NO | 8 | 7 | WEG CFW500-IOR-B IO MODULE. 0 = STOP, 1 = RUN
AC_010B | AFTER COOLER | BLWR-B DISCHARGE AFTER COOLER | NO | AC_010B.SPD_FBK | BLWR-B DISCHARGE AFTER COOLER SPEED FEEDBACK | AI | LL = X L = X H = X HH = X | 1 | 4 | ASSUME SINGLE-ENDED (LOOP-POWERED) SIGNAL NEED TO UPDATE ALARM LIMITS
AC_010B | AFTER COOLER | BLWR-B DISCHARGE AFTER COOLER | NO | AC_010B.SPD_CMD | BLWR-B DISCHARGE AFTER COOLER SPEED COMMAND | AO | NO | 5 | 5 | CONFIRM WIRING
AC_010B | AFTER COOLER | BLWR-B DISCHARGE AFTER COOLER | NO | AC_010B.RUN_ST | BLWR-B DISCHARGE AFTER COOLER RUN STATUS | DI | FTS | 7 | 8 | 0 = STOPPED, 1 = RUNNING
AC_010B | AFTER COOLER | BLWR-B DISCHARGE AFTER COOLER | NO | AC_010B.FLT_ST | BLWR-B DISCHARGE AFTER COOLER FAULT STATUS | DI | FLT | 7 | 9 | 0 = NORMAL, 1 = FAULT
AC_010B | AFTER COOLER | BLWR-B DISCHARGE AFTER COOLER | NO | AC_010B.RUN_CMD | BLWR-B DISCHARGE AFTER COOLER RUN COMMAND | DO | NO | 8 | 8 | WEG CFW500-IOR-B IO MODULE. 0 = STOP, 1 = RUN
AD_002 | REFRIGERATED AIR DRYER | COMPRESSED AIR DRYER | NO | AD_002.YC002 | COMPRESSED AIR DRYER RUN COMMAND | DO | NO | 8 | 2 | DI13/S8 - REMOTE CONTROL CONTACT. 0 = STOP, 1 = RUN NEED TO CONFIRM WIRING
AD_002 | REFRIGERATED AIR DRYER | COMPRESSED AIR DRYER | NO | AD_002.RUN_ST | COMPRESSED AIR DRYER RUN STATUS | DI | FTS | 6 | 5 | CONFIRM WIRING
AD_002 | REFRIGERATED AIR DRYER | COMPRESSED AIR DRYER | NO | AD_002.UF002 | COMPRESSED AIR DRYER FAILURE SIGNAL | DI | FLT | 6 | 6 | CONFIRM WIRING
BA_400 | GAS ANALYZER | O2 GEN. BIO GAS ANALYZER | NO | BA_400.AL1 | O2 GEN. BIO GAS ANALYZER UPGRADER OUTLET ALARM 1 | DI | FLT | 6 | 12 | NORMALLY OPEN, HELD CLOSED CONTACT. 0 = ALARM, 1 = NORMAL
BA_400 | GAS ANALYZER | O2 GEN. BIO GAS ANALYZER | NO | BA_400.AL2 | O2 GEN. BIO GAS ANALYZER UPGRADER OUTLET ALARM 2 | DI | FLT | 6 | 13 | NORMALLY OPEN, HELD CLOSED CONTACT. 0 = ALARM, 1 = NORMAL
BL_2 | BLOWER | LAG BLWR | NO | BL_2.RUN_CMD | LAG BLWR RUN COMMAND | DO | NO | 8 | 4 | DRY CONTACT. 0 = STOP, 1 = RUN. CONFIRM WIRING
BL_2 | BLOWER | LAG BLWR | NO | BL_2.SPD_FBK | LAG BLWR SPEED FEEDBACK | AI | SPD-MIS | 1 | 0 | ASSUME SINGLE ENDED, CONFIRM WIRING
BL_2 | BLOWER | LAG BLWR | NO | BL_2.SPD_CMD | LAG BLWR SPEED COMMAND | AO | NO | 5 | 0 | WEG CFW500-IOR-B IO MODULE. CONFIRM WIRING (+/- TO PINS 21/19)
BL_2 | BLOWER | LAG BLWR | NO | BL_2.RUN_ST | LAG BLWR RUNNING STATUS | DI | FTS | 6 | 9 | 0 = STOPPED, 1 = RUNNING
BL_2 | BLOWER | LAG BLWR | NO | BL_2.MAN_ST | LAG BLWR AUTO OPERATION STATUS | DI | NO | 6 | 10 | 0 = AUTO, 1 = MANUAL
BL_2 | BLOWER | LAG BLWR | NO | BL_2.FLT_ST | LAG BLWR FAULT STATUS | DI | FLT | 6 | 11 | ON LINE BETWEEN LAGOONS WSP3/4 AND DMT ZONE
CR_ACFLT | MAIN CP PWR - INPUT RELAY | AC FAULT ALARM RELAY | NO | CR_ACFLT | AC FAULT ALARM RELAY SIGNAL | DI | YES | 6 | 0 | NORMALLY OPEN, HELD CLOSED - 0 = ALARM, 1 = NORMAL
CR_ESTOP | UPS PWR - INPUT RELAY | EMERGENCY STOP ALARM RELAY | NO | CR_ESTOP | EMERGENCY STOP RELAY SIGNAL | DI | YES | 6 | 2 | NORMALLY CLOSED, HELD OPEN - 0 = NORMAL, 1 = ALARM
CR_UPS | UPS PWR - INPUT RELAY | UPS FAULT ALARM RELAY | NO | CR_UPS | UPS FAULT ALARM RELAY SIGNAL | DI | YES | 6 | 1 | NORMALLY OPEN, HELD CLOSED - 0 = ALARM, 1 = NORMAL
FM_100 | FLOW CONTROLLER | O2 DISCHARGE FM-100 FLOW CONTROLLER | NO | FM_100.F_RS | O2 DISCHARGE FLOW RATE RAW | AI | LL = X L = X H = X HH = X | 1 | 7 | ASSUME SINGLE ENDED, CONFIRM WIRING MV100 CONTROLLED BY FM100, NO PLC CONTROL
FM_100 | FLOW CONTROLLER | O2 DISCHARGE FM-100 FLOW CONTROLLER | NO | FM_100.F_SP | O2 DISCHARGE FLOW SETPOINT | AO | NO | 5 | 6 | CONFIRM WIRING MV100 CONTROLLED BY FM100, NO PLC CONTROL
MV_110 | CONTROL VALVE | O2 SHUTOFF CONTROL VALVE | NO | MV_110.POS_CMD | O2 SHUTOFF CONTROL VALVE POSITION COMMAND | AO | NO | 5 | 3 | CONFIRM WIRING
MV_110 | CONTROL VALVE | O2 SHUTOFF CONTROL VALVE | NO | MV_110.POS_CL | O2 SHUTOFF CONTROL VALVE IN CLOSED POSITION | DI | FTC | 6 | 14 | FAILED TO CLOSE ALARM
MV_110 | CONTROL VALVE | O2 SHUTOFF CONTROL VALVE | NO | MV_110.POS_OP | O2 SHUTOFF CONTROL VALVE IN OPEN POSITION | DI | FTO | 6 | 15 | FAILED TO OPEN ALARM
MV_112A | CONTROL VALVE | BLWR-A DISCHARGE CONTROL VALVE | YES | MV_112A.POS_CL | BLWR-A DISCHARGE CONTROL VALVE IN CLOSED POSITION | DI | FTC | 7 | 10 | FAILED TO CLOSE ALARM
MV_112A | CONTROL VALVE | BLWR-A DISCHARGE CONTROL VALVE | YES | MV_112A.POS_OP | BLWR-A DISCHARGE CONTROL VALVE IN OPEN POSITION | DI | FTO | 7 | 11 | FAILED TO OPEN ALARM
MV_112A | CONTROL VALVE | BLWR-A DISCHARGE CONTROL VALVE | YES | MV_112A.CL_CMD | BLWR-A DISCHARGE CONTROL VALVE CLOSE COMMAND | DO | NO | 8 | 9 | DRY CONTACT, 0 = STOP, 1 = RUN - CONFIRM WIRING
MV_112A | CONTROL VALVE | BLWR-A DISCHARGE CONTROL VALVE | YES | MV_112A.OP_CMD | BLWR-A DISCHARGE CONTROL VALVE OPEN COMMAND | DO | NO | 8 | 10 | DRY CONTACT, 0 = STOP, 1 = RUN - CONFIRM WIRING
MV_112B | CONTROL VALVE | BLWR-B DISCHARGE CONTROL VALVE | YES | MV_112B.POS_CL | BLWR-B DISCHARGE CONTROL VALVE IN CLOSED POSITION | DI | FTC | 7 | 12 | FAILED TO CLOSE ALARM
MV_112B | CONTROL VALVE | BLWR-B DISCHARGE CONTROL VALVE | YES | MV_112B.POS_OP | BLWR-B DISCHARGE CONTROL VALVE IN OPEN POSITION | DI | FTO | 7 | 13 | FAILED TO OPEN ALARM
MV_112B | CONTROL VALVE | BLWR-B DISCHARGE CONTROL VALVE | YES | MV_112B.CL_CMD | BLWR-B DISCHARGE CONTROL VALVE CLOSE COMMAND | DO | NO | 8 | 11 | DRY CONTACT, 0 = STOP, 1 = RUN - CONFIRM WIRING
MV_112B | CONTROL VALVE | BLWR-B DISCHARGE CONTROL VALVE | YES | MV_112B.OP_CMD | BLWR-B DISCHARGE CONTROL VALVE OPEN COMMAND | DO | NO | 8 | 12 | DRY CONTACT, 0 = STOP, 1 = RUN - CONFIRM WIRING
OG_003 | OXYGEN GENERATOR - PSA | O2 GENERATOR | NO | OG_003.YC003 | O2 GENERATOR RUN COMMAND | DO | NO | 8 | 3 | DRY CONTACT, 0 = STOP, 1 = RUN - CONFIRM WIRING
OG_003 | OXYGEN GENERATOR - PSA | O2 GENERATOR | NO | OG_003.RUN_ST | O2 GENERATOR RUN STATUS | DI | FTS | 6 | 7 | 0 = STOPPED, 1 = RUNNING - CONFIRM WIRING
OG_003 | OXYGEN GENERATOR - PSA | O2 GENERATOR | NO | OG_003.UF003 | O2 GENERATOR FAILURE SIGNAL | DI | FLT | 6 | 8 | 0 = NORMAL, 1 = ALARM - CONFIRM WIRING
PIT_010A | PRESSURE TRANSMITTER | BLWR-A SUCTION PRESSURE XMTR | YES | PIT_010A.P_RS | BLWR-A SUCTION PRESSURE RAW | AI | L = X H = X | 2 | 2 | ASSUME SINGLE-ENDED (LOOP-POWERED) SIGNAL NEED PART NUMBER TO CONFIRM SIGNAL WIRING
PIT_010B | PRESSURE TRANSMITTER | BLWR-B SUCTION PRESSURE XMTR | YES | PIT_010B.P_RS | BLWR-B SUCTION PRESSURE RAW | AI | L = X H = X | 2 | 3 | ASSUME SINGLE-ENDED (LOOP-POWERED) SIGNAL NEED PART NUMBER TO CONFIRM SIGNAL WIRING
PIT_012A | PRESSURE TRANSMITTER | BLWR-A DISCHARGE PRESSURE XMTR | YES | PIT_012A.P_RS | BLWR-A DISCHARGE PRESSURE RAW | AI | L = 6.0 psig H = 9.0 psig HH = 9.5 psig | 3 | 0 | ASSUME SINGLE-ENDED (LOOP-POWERED) SIGNAL NEED PART NUMBER TO CONFIRM SIGNAL WIRING
PIT_012B | PRESSURE TRANSMITTER | BLWR-B DISCHARGE PRESSURE XMTR | YES | PIT_012B.P_RS | BLWR-B DISCHARGE PRESSURE RAW | AI | L = 6.0 psig H = 9.0 psig HH = 9.5 psig | 3 | 1 | ASSUME SINGLE-ENDED (LOOP-POWERED) SIGNAL NEED PART NUMBER TO CONFIRM SIGNAL WIRING
PIT_020A | PRESSURE TRANSMITTER | DIG-A COVER PRESSURE | YES | PIT_020A.P_RS | DIG-A COVER PRESSURE RAW | AI | L = X H = X | 3 | 2 | ASSUME SINGLE-ENDED (LOOP-POWERED) SIGNAL NEED PART NUMBER TO CONFIRM SIGNAL WIRING
PIT_020B | PRESSURE TRANSMITTER | DIG-B COVER PRESSURE | YES | PIT_020B.P_RS | DIG-B COVER PRESSURE RAW | AI | L = X H = X | 3 | 3 | ASSUME SINGLE-ENDED (LOOP-POWERED) SIGNAL NEED PART NUMBER TO CONFIRM SIGNAL WIRING
PIT_3012 | PRESSURE TRANSMITTER | WSP-3 LAGOON PRESSURE 1 | YES | PIT_3012.P_RS | WSP-3 LAGOON PRESSURE 1 RAW | AI | L = X H = X | 3 | 4 | Rosemount 3051TG PASSIVE OUTPUT, 2 WIRE LOOP POWERED XMTR
PIT_3013 | PRESSURE TRANSMITTER | WSP-3 LAGOON PRESSURE 2 | YES | PIT_3013.P_RS | WSP-3 LAGOON PRESSURE 2 RAW | AI | L = X H = X | 3 | 5 | Rosemount 3051TG PASSIVE OUTPUT, 2 WIRE LOOP POWERED XMTR
PIT_3014 | PRESSURE TRANSMITTER | WSP-4 LAGOON PRESSURE 1 | YES | PIT_3014.P_RS | WSP-4 LAGOON PRESSURE 1 RAW | AI | L = X H = X | 3 | 6 | Rosemount 3051TG PASSIVE OUTPUT, 2 WIRE LOOP POWERED XMTR
PIT_3015 | PRESSURE TRANSMITTER | WSP-4 LAGOON PRESSURE 2 | YES | PIT_3015.P_RS | WSP-4 LAGOON PRESSURE 2 RAW | AI | L = X H = X | 3 | 7 | Rosemount 3051TG PASSIVE OUTPUT, 2 WIRE LOOP POWERED XMTR
RB_010A | BLOWER | DIG-A RECIRC BLWR | NO | RB_010A.RUN_CMD | DIG-A RECIRC BLWR RUN COMMAND | DO | NO | 8 | 5 | WEG CFW500-IOR-B IO MODULE. 0 = STOP, 1 = RUN
RB_010A | BLOWER | DIG-A RECIRC BLWR | NO | RB_010A.SPD_FBK | DIG-A RECIRC BLWR SPEED FEEDBACK | AI | SPDMIS | 1 | 1 | WEG CFW500-IOR-B IO MODULE. LOOP POWERED AI. SPEED MISMATCH ALARM
RB_010A | BLOWER | DIG-A RECIRC BLWR | NO | RB_010A.SPD_CMD | DIG-A RECIRC BLWR SPEED COMMAND | AO | NO | 5 | 1 | WEG CFW500-IOR-B IO MODULE. CONFIRM WIRING (+/- TO PINS 21/19)
RB_010A | BLOWER | DIG-A RECIRC BLWR | NO | RB_010A.RUN_ST | DIG-A RECIRC BLWR RUNNING STATUS | DI | FTS | 7 | 0 | WEG CFW500-IOR-B IO MODULE. 0 = STOPPED, 1 = RUNNING
RB_010A | BLOWER | DIG-A RECIRC BLWR | NO | RB_010A.FLT_ST | DIG-A RECIRC BLWR FAULT STATUS | DI | FLT | 7 | 1 | WEG CFW500-IOR-B IO MODULE. GENERAL FAULT ALARM
RB_010A | BLOWER | DIG-A RECIRC BLWR | NO | RB_010A.MAN_ST | DIG-A RECIRC BLWR AUTO/MANUAL STATUS | DI | NO | 7 | 2 | WEG CFW500-IOR-B IO MODULE. 0 = AUTO, 1 = MANUAL
RB_010B | BLOWER | DIG-B RECIRC BLWR | NO | RB_010B.RUN_CMD | DIG-B RECIRC BLWR RUN COMMAND | DO | NO | 8 | 6 | WEG CFW500-IOR-B IO MODULE. 0 = STOP, 1 = RUN
RB_010B | BLOWER | DIG-B RECIRC BLWR | NO | RB_010B.SPD_FBK | DIG-B RECIRC BLWR SPEED FEEDBACK | AI | + | 1 | 2 | WEG CFW500-IOR-B IO MODULE. LOOP POWERED AI. SPEED MISMATCH ALARM
RB_010B | BLOWER | DIG-B RECIRC BLWR | NO | RB_010B.SPD_CMD | DIG-B RECIRC BLWR SPEED COMMAND | AO | NO | 5 | 2 | WEG CFW500-IOR-B IO MODULE. CONFIRM WIRING (+/- TO PINS 21/19)
RB_010B | BLOWER | DIG-B RECIRC BLWR | NO | RB_010B.RUN_ST | DIG-B RECIRC BLWR RUNNING STATUS | DI | FTS | 7 | 3 | WEG CFW500-IOR-B IO MODULE. 0 = STOPPED, 1 = RUNNING
RB_010B | BLOWER | DIG-B RECIRC BLWR | NO | RB_010B.FLT_ST | DIG-B RECIRC BLWR FAULT STATUS | DI | FLT | 7 | 4 | WEG CFW500-IOR-B IO MODULE. GENERAL FAULT ALARM
RB_010B | BLOWER | DIG-B RECIRC BLWR | NO | RB_010B.MAN_ST | DIG-B RECIRC BLWR AUTO/MANUAL STATUS | DI | NO | 7 | 5 | WEG CFW500-IOR-B IO MODULE. 0 = AUTO, 1 = MANUAL
TIT_010A | TEMPERATURE TRANSMITTER | BLWR-A DISCHARGE TEMPERATURE XMTR | YES | TIT_010A.T_RS | BLWR-A DISCHARGE TEMPERATURE RAW | AI | H = 250 F HH = 275 F | 2 | 0 | ASSUME SINGLE-ENDED (LOOP-POWERED) SIGNAL NEED PART NUMBER TO CONFIRM SIGNAL WIRING
TIT_010B | TEMPERATURE TRANSMITTER | BLWR-B DISCHARGE TEMPERATURE XMTR | YES | TIT_010B.T_RS | BLWR-B DISCHARGE TEMPERATURE RAW | AI | H = 250 F HH = 275 F | 2 | 1 | ASSUME SINGLE-ENDED (LOOP-POWERED) SIGNAL NEED PART NUMBER TO CONFIRM SIGNAL WIRING
TIT_011A | TEMPERATURE TRANSMITTER | AFTER COOLER-A DISCHARGE TEMPERATURE XMTR | YES | TIT_011A.T_RS | AFTER COOLER-A DISCHARGE TEMPERATURE RAW | AI | LL = X L = X H = X HH = X | 2 | 4 | ASSUME SINGLE-ENDED (LOOP-POWERED) SIGNAL NEED PART NUMBER TO CONFIRM SIGNAL WIRING
TIT_011B | TEMPERATURE TRANSMITTER | AFTER COOLER-B DISCHARGE TEMPERATURE XMTR | YES | TIT_011B.T_RS | AFTER COOLER-B DISCHARGE TEMPERATURE RAW | AI | LL = X L = X H = X HH = X | 2 | 5 | ASSUME SINGLE-ENDED (LOOP-POWERED) SIGNAL NEED PART NUMBER TO CONFIRM SIGNAL WIRING
VT_010A | VIBRATION TRANSMITTER | BLWR-A DISCHARGE VIBRATION XMTR | NO | VT_010A.V_RS | BLWR-A DISCHARGE VIBRATION RAW | AI | L = X H = X | 1 | 5 | ASSUME THIS IS THE SAME AS "VS-010A" ON DIAGRAM ASSUME LOOP-POWERED) SIGNAL NEED PART NUMBER TO ONFIRM SIGNAL WIRING
VT_010B | VIBRATION TRANSMITTER | BLWR-B DISCHARGE VIBRATION XMTR | NO | VT_010B.V_RS | BLWR-B DISCHARGE VIBRATION RAW | AI | L = X H = X | 1 | 6 | ASSUME THIS IS THE SAME AS "VS-010B" ON DIAGRAM ASSUME SINGLE-ENDED (LOOP-POWERED) SIGNAL NEED PART NUMBER TO CONFIRM SIGNAL WIRING

## KCG-RIO-CP
EQUIPMENT |  |  |  | TAGS |  |  |  | I/O MODULES
EQUIPMENT ID | EQUIPMENT TYPE | EQUIPMENT DESCRIPTION | CLASSIFIED ENVIRONMENT | TAG NAME | TAG DESCRIPTION | SIGNAL TYPE | ALARMS | MODULE SLOT # | CHANNEL | DETAILS (to be deleted)
CR-01-ACFLT | INPUT RELAY | AC FAULT ALARM RELAY | NO | CR01ACFLT | AC FAULT ALARM RELAY SIGNAL | DI | FLT | 4 | 0 | NOT SURE IF WE WANT TO KEEP IT ON THIS LIST
CV-3006 | CONTROL VALVE (FY) | PIPELINE DIVERT CONTROL VALVE | YES | CV3006.POS_CMD | PIPELINE DIVERT CONTROL VALVE POSITION RAW COMMAND | AO | NO | 3 | 0 | ON LINE FROM DMT ZONE (REJECT GAS) TO LAGOON WSP3
CV-3006 | CONTROL VALVE (FY) | PIPELINE DIVERT CONTROL VALVE | YES | CV3006.POS_OP | PIPELINE DIVERT CONTROL VALVE IN OPEN POSITION | DI | FTO | 4 | 1 | ON LINE FROM DMT ZONE (REJECT GAS) TO LAGOON WSP3
CV-3006 | CONTROL VALVE (FY) | PIPELINE DIVERT CONTROL VALVE | YES | CV3006.POS_CL | PIPELINE DIVERT CONTROL VALVE IN CLOSED POSITION | DI | FTC | 4 | 2 | ON LINE FROM DMT ZONE (REJECT GAS) TO LAGOON WSP3
FIT-3006 | FLOW TRANSMITTER | PIPELINE FLOW | NO | FIT3006.F_RS | PIPELINE FLOW RATE RAW | AI | LL = X L = X H = X HH = X | 1 | 0 | E&H Prosonic G500 PASSIVE OUTPUT, 2 WIRE LOOP POWERED XMTR
FIT-3007 | FLOW TRANSMITTER | PIPELINE RETURN FLOW | NO | FIT3007.F_RS | PIPELINE RETURN FLOW RATE RAW | AI | LL = X L = X H = X HH = X | 1 | 1 | E&H Prosonic B200 PASSIVE OUTPUT, 2 WIRE LOOP POWERED XMTR
GC-3006 | GAS CHROMATOGRAPH | PIPELINE GAS | NO | GC3006.CH4_RS | PIPELINE GAS CH4 RAW | HART - P | LL = X L = X H = X HH = X | 2 | 0 | PIPELINE GC 1000 PASSIVE OUTPUT, 2 WIRE LOOP POWERED XMTR
GC-3006 | GAS CHROMATOGRAPH | PIPELINE GAS | NO | GC3006.CO2_RS | PIPELINE GAS CO2 RAW | HART - S | LL = X L = X H = X HH = X | 2 | 0 | PIPELINE GC 1000 PASSIVE OUTPUT, 2 WIRE LOOP POWERED XMTR
GC-3007 | GAS CHROMATOGRAPH | PIPELINE RETURN GAS | NO | GC3007.CH4_RS | PIPELINE RETURN GAS CH4 RAW | HART - P | LL = X L = X H = X HH = X | 2 | 1 | RECIRC GC (CH4, CO2) REJECT RNG TO LAGOON FROM INJECTION POINT PASSIVE OUTPUT, 2 WIRE LOOP POWERED XMTR
GC-3007 | GAS CHROMATOGRAPH | PIPELINE RETURN GAS | NO | GC3007.CO2_RS | PIPELINE RETURN GAS CO2 RAW | HART - S | LL = X L = X H = X HH = X | 2 | 1 | RECIRC GC (CH4, CO2) REJECT RNG TO LAGOON FROM INJECTION POINT
PIT-3006 | PRESSURE TRANSMITTER | RNG PRESSURE - PRODUCT GAS TO ONEGAS | YES | PIT3006.P_RS | RNG PRESSURE RAW | AI | L = X H = X | 1 | 3 | Rosemount 3051TG PASSIVE OUTPUT, 2 WIRE LOOP POWERED XMTR
TIT-3006 | TEMPERATURE TRANSMITTER | PIPELINE TEMPERATURE | NO | TIT3006.T_RS | PIPELINE TEMPERATURE RAW | AI | LL = X L = X H = X HH = X | 1 | 2 | PIPELINE TIT 1000 PASSIVE OUTPUT, 2 WIRE LOOP POWERED XMTR
Note on G6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Typically an open/close valve isnt going to have analog position feedback… it is available but usually its just ZSO/ZSC

## IO COUNTS
PANEL | SIGNAL TYPE | CLASSIFIED IO # | NON-CLASSIFIED IO # | TOTAL
BOP-PLC-CP | AI | 0 | 7 | 7
BOP-PLC-CP | HART - P | 0 | 7 | 7
BOP-PLC-CP | AO | 8 | 1 | 9
BOP-PLC-CP | DI | 16 | 7 | 23
BOP-PLC-CP | DO | 0 | 3 | 3
LGN-PLC-CP | AI | 14 | 8 | 22
LGN-PLC-CP | HART - P | 0 | 0 | 0
LGN-PLC-CP | AO | 0 | 7 | 7
LGN-PLC-CP | DI | 4 | 26 | 30
LGN-PLC-CP | DO | 4 | 9 | 13
KCG-RIO-CP | AI | 1 | 3 | 4
KCG-RIO-CP | HART - P | 0 | 2 | 2
KCG-RIO-CP | AO | 1 | 0 | 1
KCG-RIO-CP | DI | 2 | 1 | 3
KCG-RIO-CP | DO | 0 | 0 | 0

## NOTES & COMMENTS
EQUIPMENT | COMMENTS | RESPONSES
RB-010-A/B | Is the VFD part# CFW500F77P0T4DB20G2?
RB-010-A/B | Are we using the standard I/O module WEG CFW500-IOS supplied with the drive for our inputs from the VFD? The standard module provides 4DI/1AI/1AO/1DOR/1DOT, so only one relay output is available and second signal would need to be a transistor output. We can switch to the CFW500-IOR-B module (5DI/1AI/1AO/4DOR/1DOT) if we need both to signals to be relay outputs.
RB-010-A/B | VFD needs to be programmed and IO needs to be assigned in it to achieve required function. Who is responsible for doing this?
AC-001 | The Document says that the compressor runs on its own native demand loading and require no PLC process sequencing. Do we only need the remote Off command?
AC-001 | If using PLC Run Commands - Remote On and Off commands are separate inputs to the compressor per drawing, do we need 2 different outputs from the PLC or do use 1 relay and wire NO/NC contacts for ON/OFF?
AD-002 | The Document says that the dryer runs on its own native demand loading and require no PLC process sequencing. Do we only need the remote Off command?
OG-003 | The Document says that the Generator runs on its own native demand loading and require no PLC process sequencing. Do we only need the remote Off command?
AC-010-A/B | Are we controlling the After cooler motor from our PLC?